|  | X.Link XL-ZB(LR)IO-44 User manual |
| --- | --- |

IIOT Device node, 1 Modbus RTU channel over RS485, 1 Modbus RTU channel over Zigbee Mesh, 4 digital output, 4 digital input

## Overview

The I-IoT device is a compact and reliable industrial data acquisition and control module designed for automation and remote monitoring applications. It operates with a wide input voltage range of 8–28 VDC, ensuring stable performance in various industrial environments.

The device features one RS-485 interface supporting Modbus RTU communication and one Zigbee 2.4 GHz wireless interface, providing both wired and wireless connectivity for flexible network integration.

It is equipped with 4 optically isolated digital inputs and 4 optically isolated digital outputs, offering enhanced protection against electrical noise and signal interference. A DIP switch is provided for easy configuration of the Modbus device address, simplifying installation and field setup.

This combination of robust hardware design isolated I/O channels, and versatile communication options makes the device ideal for industrial automation, smart monitoring, and IoT gateway applications.

Contents

Overview	1

1	Features	3

2	Specifications	3

3	Applications	4

4	Pin Configuration and Functions	5

5	Modbus Register	6

6	System requirements	8

7	Configuration software	9

8	Dimensions	10

9	Ordering information	11

10	Related products	11

## Features

- High-performance MCUs based on Arm® Cortex® -M33 core with 256 Kbytes of Flash memory and 272 Kbytes of SRAM

- 8-Mbytes Quad-SPI (Winbond) Flash Memory

- Real Time Operating System

- 1 - Zigbee® mesh 2.4 GHz

- 1 - RS485 channel up to 115200 bps

- Switch Modbus address selection

- 4 - Optically Isolated Digital Input

- 4 - Optically Isolated Digital Output

- 1 - USB type C configuration

- Firmware Over-the-Air (FOTA)

- Led indicator. 1-Led power, 1-Led status, 1-Led link

## Specifications

|  |  | MIN | MAX | UNIT |
| --- | --- | --- | --- | --- |
| Voltage range | Power voltage | 8 | 28 | V |
|  | Isolated digital input voltage | 8 | 28 | V |
|  | Isolated digital output voltage | 8 | 28 | V |
| Current range |  |  |  |  |
|  | Isolated digital input current | 0.1 | 2 | A |
|  | Isolated digital output current | 0.1 | 2 | A |
| MTBF |  |  | 250000 | h |
| Temperature |  | -40 | 85 | °C |
| Humidity |  | 10 | 80 | % |

## Applications

- Remote Machine control and monitoring

- Remote Counter

- Remote Tower lamp control

- Industrial Automation

- Smart monitoring

- Remote IO, Remote sensor.

## Pin Configuration and Functions

| 1 | Power - |
| --- | --- |
|  | Power + |
|  | RS485 - A |
|  | RS485 - B |
|  | Modbus Address Selection |
|  | USB Configuration |
|  | Button |
|  | Antennal |
| 2 | Led power |
|  | Led status |
|  | Led link |
| 3 | Isolate Power - |
|  | INPUT 0 |
|  | INPUT 1 |
|  | INPUT 2 |
|  | INPUT 3 |
|  | INPUT 4 |
|  | OUTPUT 0 |
|  | OUTPUT 1 |
|  | OUTPUT 2 |
|  | OUTPUT 3 |
|  | Isolate Power + |

## Modbus Register

| Address | Size | Type | R/W | Units | Descriptions |
| --- | --- | --- | --- | --- | --- |
| 10000 | 1 | Coil Register | R/W | bit | Output 0 |
| 10001 | 1 | Coil Register | R/W | bit | Output 1 |
| 10002 | 1 | Coil Register | R/W | bit | Output 2 |
| 10003 | 1 | Coil Register | R/W | bit | Output 3 |
| 10004 | 1 | Coil Register | R/W | bit | Output 4 |
| 10005 | 1 | Coil Register | R/W | bit | Output 5 |
| 10006 | 1 | Coil Register | R/W | bit | Output 6 |
| 10007 | 1 | Coil Register | R/W | bit | Output 7 |
| 10008 | 1 | Coil Register | R/W | bit | Reset counter 0 |
| 10009 | 1 | Coil Register | R/W | bit | Reset counter 1 |
| 10010 | 1 | Coil Register | R/W | bit | Reset counter 2 |
| 10011 | 1 | Coil Register | R/W | bit | Reset counter 3 |
| 10012 | 1 | Coil Register | R/W | bit | Reset counter 4 |
| 10013 | 1 | Coil Register | R/W | bit | Reset counter 5 |
| 10014 | 1 | Coil Register | R/W | bit | Reset counter 6 |
| 10015 | 1 | Coil Register | R/W | bit | Reset counter 7 |
| 20000 | 1 | Discrete Register | R | bit | Input 0 |
| 20001 | 1 | Discrete Register | R | bit | Input 1 |
| 20002 | 1 | Discrete Register | R | bit | Input 2 |
| 20003 | 1 | Discrete Register | R | bit | Input 3 |
| 20004 | 1 | Discrete Register | R | bit | Input 4 |
| 20005 | 1 | Discrete Register | R | bit | Input 5 |
| 20006 | 1 | Discrete Register | R | bit | Input 6 |
| 20007 | 1 | Discrete Register | R | bit | Input 7 |
| 30000 | 16 | Holding register | R/W | Integer | Setup input mask for output 0 set level 0x00 : output 0 off 0x01 : I0 trigger -> O0 On 0x02 : I1 trigger -> O0 On 0x04 : I2 trigger -> O0 On 0x08 : I3 trigger -> O0 On 0x03 : I0 & I1 trigger -> O0 On … |
| 30001 | 16 | Holding register | R/W | Integer | Setup input mask for output 1 set level |
| 30002 | 16 | Holding register | R/W | Integer | Setup input mask for output 2 set level |
| 30003 | 16 | Holding register | R/W | Integer | Setup input mask for output 3 set level |
| 30004 | 16 | Holding register | R/W | Integer | Setup input mask for output 1 set level |
| 30005 | 16 | Holding register | R/W | Integer | Setup input mask for output 2 set level |
| 30006 | 16 | Holding register | R/W | Integer | Setup input mask for output 3 set level |
| 30007 | 16 | Holding register | R/W | Integer | Setup input mask for output 3 set level |
| 30008 | 16 | Holding register | R/W | Integer | Set timer0 period (ms) |
| 30009 | 16 | Holding register | R/W | Integer | Set timer1 period (ms) |
| 30010 | 16 | Holding register | R/W | Integer | Set timer2 period (ms) |
| 30011 | 16 | Holding register | R/W | Integer | Set timer3 period (ms) |
| 30012 | 16 | Holding register | R/W | Integer | Set Output mask when timer 0 trigger |
| 30013 | 16 | Holding register | R/W | Integer | Set Output mask when timer 1 trigger |
| 30014 | 16 | Holding register | R/W | Integer | Set Output mask when timer 2 trigger |
| 30015 | 16 | Holding register | R/W | Integer | Set Output mask when timer 3 trigger |
| 30012 | 16 | Holding register | R/W | Integer | Set Output mask when timer 4 trigger |
| 30013 | 16 | Holding register | R/W | Integer | Set Output mask when timer 5 trigger |
| 30014 | 16 | Holding register | R/W | Integer | Set Output mask when timer 6 trigger |
| 30015 | 16 | Holding register | R/W | Integer | Set Output mask when timer 7 trigger |
| 40000 | 8 | Input register | R | string | Serial number |
| 40016 | 16 | Input register | R | Integer | Counter 0 |
| 40017 | 16 | Input register | R | Integer | Counter 1 |
| 40018 | 16 | Input register | R | Integer | Counter 2 |
| 40019 | 16 | Input register | R | Integer | Counter 3 |
| 40020 | 16 | Input register | R | Integer | Timer 0 counter |
| 40021 | 16 | Input register | R | Integer | Timer 1 counter |
| 40022 | 16 | Input register | R | Integer | Timer 2 counter |
| 40023 | 16 | Input register | R | Integer | Timer 3 counter |

## System requirements

- Windows® OS (XP, 7, 8 and 10), Linux® or MacOS™

- USB Type-A to Type-C cable

- USB Driver

## Configuration software

- Software : X.LinkConfig

Main Selection Page

Zigbee Parameter Configuration Page

RS485 Configuration Page

Checking Signal Device Page (Only using with Gateway)

## Dimensions

## Ordering information

| Part number | RS-485 | Zigbee | LORA | Isolated Digital Input | Isolated Digital Output |
| --- | --- | --- | --- | --- | --- |
| XL-ZBIO-44 | Yes | Yes |  | 4 CH | 4 CH |
| XL-ZBIO-8I | Yes | Yes |  | No | 8 CH |
| XL-ZBIO-8O | Yes | Yes |  | 8 CH | No |
| XL-ZBIO-420I | Yes | Yes |  | 2 CH | 6 CH |
| XL-LRIO-44 | Yes |  | Yes | 4 CH | 4 CH |
| XL-LRIO-8I | Yes |  | Yes | No | 8 CH |
| XL-LRIO-8O | Yes |  | Yes | 8 CH | No |
| XL-LRIO-420I | Yes |  | Yes | 2 CH | 6 CH |

## Related products

XLink- Gateway: X.Link-GW-ZB485

XL can operate in pairs for parallel transmission and reception as a way to eliminate physical wired connections, or operate in a mesh network to aggregate data from multiple nodes via Zigbee or Lora networks before transmitting it to a server via Ethernet.

XL-Gateway is a gateway that converts data on Zigbee/Lora networks using various protocols such as Modbus RTU, Bacnet, etc., to a server/cloud via Rest API, MQTT, etc.

Innovating Industrial IoT Solutions

_________________________________________________________________________

SYNAPTIX TECHNOLOGY JSC

Email : 	info@synaptix-io.com

Phone : 	+84-972141491

 Website : 	http://synaptix-io.com

Location : 	2nd Floor, PZ4 Building, Vinhomes Smart city, Hanoi City